Project Team: Group

ENEL 674: Industrial and Commercial Power System

Department of Electrical and Software Engineering, University of Calgary

Group Members:

Rajvinder Singh Mann

Raj Patel

Senil Manjarawala

Instructor: Jazayeri, Seyed Pouyan (Yani)

Milestone 1

Based on the initial calculations of equipment sizes, this report includes the design of the overall equipment layout. This is a preliminary stage. At this point, this report would be able to give a "client" recommendations or limitations regarding their needs, as well as the approximate amount needed, equipment space requirements, and any additional space, rooms, or buildings needed. These layouts take into consideration aspects such as load distribution, cable routing, and accessibility for maintenance in order to maximize the electrical system's efficiency and safety. This report will be divided into few sections to ease the documentation process.

Normal Power Single Line Diagram

An electrical distribution system for a building or facility is shown in a simplified image called a Normal Power Single Line Diagram (SLD). It offers a concise and understandable summary of the parts of electricity distribution and how they are connected. Standardized symbols are usually used in single line diagrams to depict different electrical equipment and devices. Some components that would be seen in this report is power source, circuit breakers and transformers.

Emergency Power Single Line Diagram

A schematic representation of the electrical distribution system that focuses on parts associated with emergency power sources and distribution is called an Emergency Power Single Line Diagram (SLD). Understanding how power is delivered in emergency situations, like power outages, requires this kind of illustration. Some key elements that can be seen in this diagram include emergency power source, transfer switches and emergency lighting.

Lighting Layout Drawing

To make sure the lighting system in the building is appropriately built, implemented, and maintained, it is imperative to have a lighting layout drawing. The drawing includes comprehensive information about the location, kind, voltage and wattage requirements, number of lights, and other important features of the light fixtures. The correct operation of the lighting system and the security of the building's residents depend on this information. Thus, it is essential to have a lighting arrangement drawing in this structure to guarantee the effective and safe installation and maintenance of the lighting system. Proper drawing is required, and it must be very specific and clean to be view by the engineering team.

For this projects, three types of LED lights have been selected. These three lights are distributed accordingly based on the room’s requirements. Below are the three types of LED lights:

- 38W LED light (2x4 troffer module)

- 21W LED light (2x2 troffer module)

- 9W Spotlight

The 38W LED is an ambient lighting and it is used in the bigger rooms such as mechanical, telecom and electrical rooms. These rooms are important as it has mechanical and electrical equipment, and it should be luminated properly for safety purposes as regular maintenance or scheduled checking will be done in these areas. Even the kitchen will be installed with this light as there are sharp objects that will be used here. The 21W LED light is similar to the 38 LED light but instead of having a 2x4 panel, it has a 2x2 panel. Therefore, it has less lumens. This type of light is used in areas such as classrooms, offices, and storage as it is sufficient to light these areas up. The 9W spotlight will be installed in the exhibit gallery as there will be art displays such as painting which would need concentrated illuminance on them. These three lights have an efficacy of 110 and above, therefore they are highly efficient LED’s.

In order to calculate the number of illuminates needed, few assumptions have been made. Below is the list of assumptions made:

- Room cavity in the range of 5-8 ft.

- Light Loss Factor (LLF) is 0.9.

- If the Room Cavity Ratio (RCR) is more than 10, RCR = 10 is used for the luminaire cut sheets.

- Coefficients of Utilization of 80/30/20 is used.

Figure 1: Lux requirements.

Desired illuminance is assumed based on the table below:

The dimensions of each room are retrieved from AUTCAD base plan layout, and it has been scaled accordingly. The formula’s used to calculate the number of lights needed is shown below:

RCR= 5 x room cavity height x (L+W)area of room

Coefficient of utilization (CU)=Based on datasheet of light

Number of Lights= Desired fc x area of roomLumen of light x CU x LLF

By using the formulas above, the calculated results for each room are tabulated below:

Table 1: Values for each room

| Room | RCR | CU | LLF | Number of Lights |
| --- | --- | --- | --- | --- |
| Mechanical 203 | 3.9 | 0.62 | 0.9 | 7 |
| Telecom | 6.9 | 0.43 | 0.9 | 3 |
| Classroom 121 | 3.24 | 0.63 | 0.9 | 9 |
| Exhibit Gallery | 4.5 | 0.57 | 0.9 | 9 |
| Exhibit Gallery Spotlight | 4.5 | 0.51 | 0.9 | 3 |
| Tea Ceremony | 8.33 | 0.37 | 0.9 | 2 |
| Foyer | 11.67 | 0.31 | 0.9 | 2 |
| Classroom 101 | 3.24 | 0.63 | 0.9 | 2 |
| Closet | 12.5 | 0.31 | 0.9 | 1 |
| Women's WR | 4.69 | 0.59 | 0.9 | 3 |
| Men's WR | 6.89 | 0.43 | 0.9 | 3 |
| Water Meter | 12.5 | 0.31 | 0.9 | 1 |
| Stair | 22.6 | 0.31 | 0.9 | 3 |
| Corr | 15.86 | 0.31 | 0.9 | 1 |
| Jan | 14.58 | 0.31 | 0.9 | 1 |
| Snack Preparation | 12.56 | 0.51 | 0.9 | 1 |
| Kitchenette | 3.03 | 0.7 | 0.9 | 4 |
| Kitchenette Spotlight | 3.03 | 0.42 | 0.9 | 2 |
| Commons | 2.93 | 0.7 | 0.9 | 4 |
| Vestibule | 10.1 | 0.31 | 0.9 | 3 |
| Staff | 6.0 | 0.47 | 0.9 | 3 |
| Mechanical 117 | 10 | 0.31 | 0.9 | 2 |
| Admin Office | 6.25 | 0.43 | 0.9 | 3 |
| ED Office | 5.0 | 0.54 | 0.9 | 3 |
| Information and Gift Shop | 3.38 | 0.65 | 0.9 | 7 |
| Storage 114 | 12.5 | 0.31 | 0.9 | 1 |
| Yukata | 7.14 | 0.39 | 0.9 | 3 |
| Storage 111 | 8.75 | 0.37 | 0.9 | 1 |
| Cultural Activity Room | 1.9 | 0.93 | 0.9 | 8 |
| Electrical Room | 6.89 | 0.43 | 0.9 | 3 |

In order to calculate the number of lights required by the rooms, the dimension of the room is also needed. Below is the dimension of each room that were scaled accordingly from the base layout using AUTOCAD.

Table 2: Calculation for number of lights

| Room | Light Type | Proposed No. Lights | Width (ft) | Length (ft) | Required lux | Required fc | Lumens of light |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Mechanical 203 | 38 | 7.00 | 20.00 | 21.00 | 450.00 | 41.81 | 4656 |
| Telecom | 38 | 3.00 | 8.00 | 21.00 | 400.00 | 37.16 | 4656 |
| Classroom 121 | 21 | 9.00 | 16.00 | 22.00 | 400.00 | 37.16 | 2571 |
| Exhibit Gallery | 21 | 9.00 | 12.00 | 22.00 | 475.00 | 44.13 | 2571 |
| Exhibit Gallery Spotlight | 9 | 3.00 | 12.00 | 22.00 | 476.00 | 44.22 | 1057 |
| Tea Ceremony | 21 | 2.00 | 6.00 | 14.00 | 150.00 | 13.94 | 2571 |
| Foyer | 21 | 2 | 6.00 | 8.00 | 300.00 | 27.87 | 2571 |
| Classroom 101 | 21 | 9 | 16.00 | 22.00 | 400.00 | 37.16 | 2571 |
| Closet | 21 | 1 | 4.00 | 6.00 | 150.00 | 13.94 | 2571 |
| Women's WR | 21 | 3 | 16.00 | 14.00 | 200.00 | 18.58 | 2571 |
| Men's WR | 21 | 3 | 10.50 | 13.00 | 200.00 | 18.58 | 2571 |
| Water Meter | 21 | 1 | 4.00 | 6.00 | 150.00 | 13.94 | 2571 |
| Stair | 21 | 3 | 3.20 | 30.00 | 200.00 | 18.58 | 2571 |
| Corr | 21 | 1 | 5.20 | 8.00 | 200.00 | 18.58 | 2571 |
| Jan | 21 | 1 | 4.00 | 6.00 | 150.00 | 13.94 | 2571 |
| Snack Preparation | 21 | 1 | 4.00 | 12.00 | 200.00 | 18.58 | 2571 |
| Kitchenette | 38 | 4 | 18.00 | 22.00 | 300.00 | 27.87 | 4656 |
| Kitchenette | 9 | 2 | 18.00 | 22.00 | 300.00 | 27.87 | 1057 |
| Commons | 38 | 4 | 22.00 | 36.00 | 300.00 | 27.87 | 4656 |
| Vestibule | 21 | 3 | 5.00 | 11.00 | 250.00 | 23.23 | 2571 |
| Staff | 21 | 3 | 10.00 | 10.00 | 375.00 | 34.84 | 2571 |
| Mechanical 117 | 38 | 2 | 10.00 | 8.00 | 400.00 | 37.16 | 4656 |
| Admin Office | 21 | 3 | 8.00 | 12.00 | 320.00 | 29.73 | 2571 |
| ED Office | 21 | 3 | 12.00 | 12.00 | 320.00 | 29.73 | 2571 |
| Information and Gift Shop | 21 | 7 | 20.00 | 16.00 | 350.00 | 32.52 | 2571 |
| Storage 114 | 21 | 1 | 6.00 | 4.00 | 150.00 | 13.94 | 2571 |
| Yukata | 21 | 3 | 14.00 | 6.00 | 300.00 | 27.87 | 2571 |
| Storage 111 | 21 | 1 | 6.00 | 8.00 | 150.00 | 13.94 | 2571 |
| Cultural Activity Room | 38 | 8 | 48.00 | 24.00 | 275.00 | 25.55 | 4656 |
| Electrical Room | 38 | 3 | 6.00 | 15.00 | 450.00 | 41.81 | 4565 |

After calculating the number of lights needed for each room, it is important to develop a luminaire schedule. A luminaire schedule is a document that gives specific details on the luminaires (light fixtures) that will be utilized in this project. It is used in lighting design and engineering. It serves as a reference for designers and contractors ensuring all the lighting requirements are met and most importantly, it is installed correctly.

Cost Analysis

In this section, few options of light models are suggested. This analysis takes into account various aspects, including the cost of the initial purchase, energy efficiency, maintenance costs, and possible long-term savings. The most affordable option that satisfies the building's functional and aesthetic needs by contrasting several lighting types is presented. In order to create an environment that is both well-lit and economically sustainable, this strategy balances initial investment with ongoing operational and energy costs to guarantee the best possible resource utilization. The table below shows option 1 of the lighting models.

Option 1

This option was demonstrated in milestone 1. It has a good balance between pricing affordability and the spacing required for the installation of the lighting. But to give more choices for the lights, another two options have been developed for milestone 2.

| Type | Model | Price (CAD) | Quantity | Total (CAD) |
| --- | --- | --- | --- | --- |
| 1 | 24EN-LD2-45-UNV-L835-CD1-U | $297.43 | 33 | $9815.19 |
| 2 | 22EN-LD2-25-UNV-L835-CD1-U | $193.05 | 61 | $11776.05 |
| 3 | T271L 9W Arc LED | $116.66 | 5 | $583.3 |
| Gross Total (CAD) |  | $21773.59 |  |  |

Option 2

Type 1 light has the same specifications as the light in option 1 with very similar efficacy and control system but is less in terms of lumens per watt produced. Therefore, more lights are required to be installed if we would like to use this light as an option. Instead of using 33 modules, we would have to use 42 modules, but it will still be cheaper than option 1. But this might not be very convenient as some rooms such as kitchenette uses this type of light and adding more lights to the room might be challenge.

Type 2 light is another version with a better efficacy, but more lumens produced. Therefore, the number of lights may be reduced in some rooms. The room where the number of lights can be decreased is classrooms, exhibit gallery, offices and information and gift shop. With the number of lumens of 3200, it is a good option as its price is lower than option 1.

Type 3 light is a track or also known as spotlight. This type of light is needed for the exhibit gallery where it is used to illuminate artwork. It is also used on the countertop of the kitchenette. It has a slightly higher number of lumens produced which is about 1460 lumens. It has similar dimensions as well as the light in option 1. The number of lights installed would remain the same.

| Type | Model | Price (CAD) | Quantity | Total (CAD) |
| --- | --- | --- | --- | --- |
| 1 | Lithonia CPX-2X4 LED Flat Panel Troffer Light | $144.99 | 42 | $6299.58 |
| 2 | Lithonia CPX-2X2 LED Flat Panel | $132.35 | 55 | $7279.25 |
| 3 | Eglo 95633A Salto LED Track Light | $129.00 | 5 | $645.00 |
| Gross Total (CAD) |  | $14223.83 |  |  |

Option 3

In this option, the first light type which is the 2x4 LED troffer has cheaper price compared to other two options but due to the number of lumens produced is at 3300 lumens, slightly more panels would have to be installed. The same goes for the type 2 panel where its lumens output is about 2400. The type 3 light has the same specifications as the other two options, therefore the number of lights needed would be the same as the other options.

| Type | Model | Price (CAD) | Quantity | Total (CAD) |
| --- | --- | --- | --- | --- |
| 1 | Commercial Electric 2x4 Integrated LED Flat Panel Troffer | $124.00 | 48 | $5952.00 |
| 2 | Commercial Electric 2x2 Integrated LED Flat Panel Troffer | $89.88 | 75 | $6749.25 |
| 3 | Tech Lighting 700FJBRK8272006S Track Light | $100.00 | 5 | $500.00 |
| Gross Total (CAD) |  | $13201.25 |  |  |

Luminaire Schedule

Table 3: Luminaire schedule

| No | Area | Luminaire | Description | Mounting | Wattage (W) | Lumens | Manufacture | Part Number | Remarks | Driver | CCT | CRI | Controls | Voltage | Efficacy |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Mechanical 203 | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 122.5 |
| 2 | Telecom | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 123.5 |
| 3 | Commons | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 123.5 |
| 4 | Cultural Activity Room | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 123.5 |
| 5 | Kitchenette | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 123.5 |
| 6 | Kitchenette | Recessed Luminaire | The ultra-efficient optical system of the Arc LED trac fixture maximizes efficiency while minimizing fixture depth. It approximates the light output and distribution of 60-75W PAR30 halogen lamps, utilizing about 20% of the energy and having a rated life of 50,000 hours | Ceiling Mounted | 9 | 1057 | Acuity Brands | ARC™ 9W LED T271L G2 27K 80CRI NFL | Compatible with Trac-Master 1- or 2-circuit tracing, Trac-Lites tracing, monopoints, and specialized mountings; also UL certified Suitable for ConTech® LT Series tracks; precise spring action from copper alloy contacts prevents arcing and takes up no set; on/off switch included; patented polarity arrows embossed on adapter bottom; spring-loaded positive latch with polarity arrows embossed secures trac light to trac; two-position power contact provided for two-circuit application. | • Dimmable using high quality reverse phase electronic low voltage (ELV) dimmers | 2700K | 80 | Timer | 120 | 117 |
| 7 | Mechanical 117 | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >80 | Integral/Motion Sensor | 120 | 123.5 |
| 8 | Electrical Room | Recessed Luminaire | Long-life LED system coupled with electrical driver to deliver optimal performance. Projected life is 100,000 hours at 92% lumen output. | Ceiling Mounted | 38 | 4656 | Cooper Lighting Solutions | 24EN-LD2-45-UNV- L835-CD1-U | For strength, stiffness, and the removal of gaps, end plates are firmly fastened with screws. For further security and ease, end plates offer an additional grid-lock feature. There are four extra places where the fixture end can be suspended. Big access plate for connecting supplies | 0-10V dimming driver | 3000K | >81 | Integral/Motion Sensor | 120 | 123.5 |
| 9 | Classroom 121 | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 10 | Classroom 101 | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 11 | Foyer | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 12 | Jan | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 13 | Staff | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 14 | ED Office | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 15 | Admin Office | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 16 | Yakuta | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 17 | Info and Gift shop | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <85 | Integral/Motion Sensor | 120 | 122.53 |
| 18 | Closet | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <86 | Integral/Motion Sensor | 120 | 122.53 |
| 19 | Water Meter | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <87 | Integral/Motion Sensor | 120 | 122.53 |
| 20 | Storage 114 | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <88 | Integral/Motion Sensor | 120 | 122.53 |
| 21 | Storage 111 | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <89 | Integral/Motion Sensor | 120 | 122.53 |
| 22 | Tea ceremony | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <90 | Integral/Motion Sensor | 120 | 122.53 |
| 23 | Stair | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <91 | Integral/Motion Sensor | 120 | 122.53 |
| 24 | Corr | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <92 | Integral/Motion Sensor | 120 | 122.53 |
| 25 | Vestibule | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <93 | Integral/Motion Sensor | 120 | 122.53 |
| 26 | Exhibit Gallery | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <94 | Integral/Motion Sensor | 120 | 122.53 |
| 27 | Exhibit Gallery | Recessed Luminaire | The ultra-efficient optical system of the Arc LED trac fixture maximizes efficiency while minimizing fixture depth. It approximates the light output and distribution of 60-75W PAR30 halogen lamps, utilizing about 20% of the energy and having a rated life of 50,000 hours | Ceiling Mounted | 9 | 1057 | Acuity Brands | ARC™ 9W LED T271L G2 27K 80CRI NFL | Compatible with Trac-Master 1- or 2-circuit tracing, Trac-Lites tracing, monopoints, and specialized mountings; also UL certified Suitable for ConTech® LT Series tracks; precise spring action from copper alloy contacts prevents arcing and takes up no set; on/off switch included; patented polarity arrows embossed on adapter bottom; spring-loaded positive latch with polarity arrows embossed secures trac light to trac; two-position power contact provided for two-circuit application. | • Dimmable using high quality reverse phase electronic low voltage (ELV) dimmers | 2700K | 80 | Timer | 120 | 117 |
| 28 | Snack Preparation | Recessed Luminaire | High performance efficacy up to 143 lumens per watt. Over 60% energy savings when compared to a fluorescent troffer | Ceiling Mounted | 21 | 2571 | Cooper Lighting Solutions | 22EN-LD2-25-UNV- L835-CD1-U | Screws are used to firmly fasten end plates to provide strength, stiffness, and the absence of gaps. For convenience and safety, end plates offer an optional grid-lock mechanism. There are four spare fixture end suspension points available. Generous access plate for connecting the supply. | 0-10V continuous dimming driver | 3500K | <91 | Integral/Motion Sensor | 120 | 122.53 |

Power Layout Drawing

An extensive engineering design known as a "Power Layout Drawing" offers a thorough overview of the placement and physical configuration of different electrical components inside a building. Engineers, electricians, and other parties involved in the installation, upkeep, or change of the electrical system use this drawing, which is a crucial component of the electrical design documentation. Major electrical equipment locations, cable routing, and other relevant information are included in the drawing.

Service Sizing Calculation

In the context of electrical systems, "service sizing calculation" refers to figuring out the right size of electrical service that will supply electricity to a structure or facility. This entails figuring out how much capacity is required to meet the projected demand for electricity. The rated capacity, which is typically measured in amperes (A) or kilovolt-amperes (kVA), is used to express the service size.

For the calculation of basic load, or also known as non-continuous load, the formula below is utilised:

Basic Load kW=Area m2 x Watts kWm2

The basic load that was calculated is 40.781 kW. This basic load also includes a 30HP fire pump and will only be used in case of an emergency.

In order to calculate the continuous load, the formula below is used:

Total Continuous Load kW= Σ Rated Loads (kW)

The continuous load has a value of 72.415 kW. The continuous load includes mechanical equipment’s and lighting equipment’s. The reason why lighting is included as a continuous load because in a commercial building, lighting is generally used more that 3 hours.

The summation of the of the continuous and non-continuous load will be the total max operating load as shown below:

Total Max Operating Load kW=

Σ Non Continuous Loads kW+ Σ Continuous Loads (kW)

=72.415+40.787=113.2 kW

In order to determine the Service Size Required (AMPS), the formula below is used:

Minimum Service Size Ampacity A=

Non Continuous Loads W+Continuous Loads Wx 1.25Rated Voltage

The calculated AMPS is 364.45A. Therefore, a 600A service to the building would be ideal to account for excess load.

Regarding the transformer kVA rating, the formula shown below is used:

S= 3 x V x I

Which results in 216.15 kVA. Therefore, a 225 kVA would be recommended to be used for this project. Next would be the breaker size calculation. The breaker is important when there is an event of overcurrent, it will cut the circuit. In short, it protects the circuit. The formula would be as below:

I= S3 x V

The current that was calculated is 750 A. Therefore, an 800 A Molded Case Circuit Breaker (MCCB).

Next step is calculating conductor size transformer. The formula shown below is used:

No of conductors per ϕ= AmpsAmpacity

By using this formula, the value calculated was close to 1 which means that it would be 1 conductor per phase. So there total of 4 conductors 3 for each phase and 1 conductor for neutral.

Mechanical Schedule

In the context of engineering and construction, a mechanical schedule is a document that provide comprehensive details of the mechanical systems and equipment that will be placed in a structure or facility. A vital component of the entire project paperwork, this schedule is used by a number of stakeholders, including facility managers, engineers, contractors, and architects. A mechanical schedule's contents aid in ensuring that mechanical components are appropriately planned, acquired, and installed.

Panel Schedule

A Panel Schedule is a written record or illustration that offers comprehensive details regarding the power distribution inside an electrical panel. To understand the arrangement, capability, and use of the panel's circuits requires knowledge of this timetable. Panel schedules are used by engineers, electricians, and maintenance staff to plan, schedule, and troubleshoot electrical work.